|  |  |  |  |  |
| --- | --- | --- | --- | --- |
|  |  | | |  |
| **Huawei Zabbix Plug-in** | | |
| **User Guide** | | |
| **Issue** | **01** | |
| **Date** | **2020-11-11** | |
|  | | | | |
|  | HUAWEI TECHNOLOGIES CO., LTD. | |  |  |

|  |
| --- |
| **Copyright © Huawei Technologies Co., Ltd. 2020. All rights reserved.**  No part of this document may be reproduced or transmitted in any form or by any means without prior written consent of Huawei Technologies Co., Ltd.  **Trademarks and Permissions**  and other Huawei trademarks are trademarks of Huawei Technologies Co., Ltd.  All other trademarks and trade names mentioned in this document are the property of their respective holders.  **Notice**  The purchased products, services and features are stipulated by the contract made between Huawei and the customer. All or part of the products, services and features described in this document may not be within the purchase scope or the usage scope. Unless otherwise specified in the contract, all statements, information, and recommendations in this document are provided "AS IS" without warranties, guarantees or representations of any kind, either express or implied.  The information in this document is subject to change without notice. Every effort has been made in the preparation of this document to ensure accuracy of the contents, but all statements, information, and recommendations in this document do not constitute a warranty of any kind, express or implied. |

|  |  |
| --- | --- |
| Huawei Technologies Co., Ltd. | |
| Address: | Huawei Industrial Base  Bantian, Longgang  Shenzhen 518129  People's Republic of China |
| Website: | <https://e.huawei.com> |
|  |  |

About This Document

Purpose

This document describes the functions and usage of Huawei Zabbix plug-in. The Huawei Zabbix plug-in is provided as a Zabbix template. Users can directly use it or use it for secondary development. The Zabbix plug-in can be used to monitor the iBMC, HMM, CCU component, EMM (MM921), or SWI (CX320/CX621).

Intended Audience

This document is intended for:

* Technical support engineers
* System maintenance engineers

Symbol Conventions

The symbols that may be found in this document are defined as follows.

| Symbol | Description |
| --- | --- |
|  | Indicates an imminently hazardous situation which, if not avoided, will result in death or serious injury. |
|  | Indicates a potentially hazardous situation which, if not avoided, could result in death or serious injury. |
|  | Indicates a potentially hazardous situation which, if not avoided, could result in minor or moderate injury. |
|  | Indicates a potentially hazardous situation which, if not avoided, could result in equipment damage, data loss, performance deterioration, or unanticipated results.  NOTICE is used to address practices not related to personal injury. |
|  | Calls attention to important information, best practices, and tips.  NOTE is used to address information not related to personal injury, equipment damage, and environment deterioration. |

Change History

| Issue | Date | Description |
| --- | --- | --- |
| 01 | 2020-11-11 | This issue is the first official release. |

Contents

[About This Document ii](#_Toc56413260)

[1 Zabbix Template Introduction 1](#_Toc56413261)

[2 Template Functions 2](#_Toc56413262)

[3 Template Configuration 4](#_Toc56413263)

[3.1 Configuring the iBMC, HMM, CCU, EMM, or SWI 4](#_Toc56413264)

[3.1.1 Configuring the iBMC or HMM 4](#_Toc56413265)

[3.1.2 Configuring the CCU 4](#_Toc56413266)

[3.1.3 Configuring the EMM/SWI 4](#_Toc56413267)

[3.1.4 Setting SNMP Trap 5](#_Toc56413268)

[3.2 Importing a Template 6](#_Toc56413269)

[3.2.1 Importing a ValueMap Template 6](#_Toc56413270)

[3.2.2 Importing an iBMC, HMM, CCU, EMM, or SWI Template 7](#_Toc56413271)

[3.3 Configuring a Template 7](#_Toc56413272)

[3.3.1 Configuring the Huawei Server HMM Template or Huawei Server iBMC Template 7](#_Toc56413273)

[3.3.2 Configuring the Huawei CCU Template 8](#_Toc56413274)

[3.4 Adding a Host 8](#_Toc56413275)

[4 Zabbix share 10](#_Toc56413276)

# Zabbix Template Introduction

The Huawei Zabbix plug-in is provided as a Zabbix template. Users can directly use it or use it for secondary development. The Zabbix plug-in can be used to monitor the iBMC, HMM, CCU component, EMM (MM921), or SWI (CX320/CX621).

Hardware Compatibility, Compatible Versions, and Version Dependencies

For details about the hardware compatibility, compatible versions, and version dependencies of the Zabbix plug-in, use the [Management Software Compatibility Query Tool](http://support-it.huawei.com/server-plugin-compatible/#/home).

Zabbix Template Names

* Huawei Server ValueMap V1.2.xml
* Huawei Server iBMC Template V1.2.xml
* Huawei CCU Template V1.2.xml
* Huawei Server HMM Template V1.2.xml
* Huawei Chassis EMM Template V1.2.xml
* Huawei Chassis SWI Template V1.2.xml

# Template Functions

iBMC Template

**Monitoring** page:

* **Latest data** tab page: CPU, fan, hard disk, iBMC system information, memory, power supply, RAID controller card, and temperature
* **Problems and triggers** tab page: system health status, CPU status, fan status, power supply status, hard disk status, and memory status
* **Graphs** tab page: inlet temperature, power consumption, system CPU usage, averagePower, peakPower, presentSystemPower and system memory usage

**Inventory** page: type, name, OS, serial number, tag, and MAC address

HMM Template

**Monitoring** page:

* **Latest data** tab page: CPU, fan, power supply, switch, system information, and temperature
* **Problems and triggers** tab page: system health, chassis health, SMM health, blade status, fan status, power supply status, and switch status
* **Graphs** tab page: ambient temperature, inlet temperature, LSW temperature, outlet temperature, real-time chassis power, blade CPU power, blade inlet temperature, real-time blade power, and blade system CPU usage

**Inventory** page: type, name, OS, serial number, tag, and MAC address

CCU Template

**Monitoring** page:

* **Latest data** tab page: system software version, system hardware version, module name, MAC address, photoelectric liquid level sensor detection result, float liquid level sensor detection result, water sensor detection result, solenoid valve actuator detection result, door status sensor detection result, and temperature and humidity sensor detection result
* **Problems** tab page: photoelectric liquid level alarm, float liquid level alarm, liquid leakage alarm, proportional valve fault alarm, door status alarm, and temperature and humidity fault alarm
* **Graphs** tab page: temperature and humidity inside and outside the cabinet

**Inventory** page: system software version, system hardware version, module name, and MAC address

EMM/SWI Template

**Monitoring** page:

* **Latest data** tab page: alarm serial number, sensor name, event description, alarm severity, event code, event parameter 2, event parameter 3, server ID, server location, and alarm time of a trap event
* **Problems** tab page: alarm information about the trap event



If the EMM/SWI alarm severity is changed, you need to manually modify the corresponding template on the Zabbix WebUI. The procedure is as follows:

Log in to the Zabbix WebUI.

Choose **Configuration > Templates**. The **Templates** page is displayed.

In the template list, click **Triggers** in the row where the template is located. The **Triggers** page is displayed.

In the alarm list, click the name of the alarm to be modified. The page for modifying the alarm information is displayed.

Change the severity of the alarm event.

# Template Configuration

[3.1 Configuring the iBMC, HMM, CCU, EMM, or SWI](#_EN-US_TOPIC_0136136909)

[3.2 Importing a Template](#_EN-US_TOPIC_0136136911)

[3.3 Configuring a Template](#_EN-US_TOPIC_0262129259)

[3.4 Adding a Host](#_EN-US_TOPIC_0262130078)

## Configuring the iBMC, HMM, CCU, EMM, or SWI

### Configuring the iBMC or HMM

Enable SNMPv2c.

Configure a community name.

----End

### Configuring the CCU

Configure the IP address, subnet mask, and gateway for the CCU.

Configure the SNMPv3 user name, authentication key, and encryption key for the CCU.

----End

### Configuring the EMM/SWI

Enable the SNMP trap protocol.

Configure the trap version (SNMPv2c or SNMPv3).

Set the trap mode to the precise alarm mode.

Configure the trap server.

----End

### Setting SNMP Trap

For the EMM/SWI, you need to set the SNMP trap on the Zabbix background.

Prerequisites

* SNMPTT, net-snmp, net-snmp-utils and net-snmp-perl of the latest versions have been installed on Zabbix.
* The firewall is disabled.

Procedure

The following uses SNMPTT as an example. For details, see the [official Zabbix website](https://www.zabbix.com/documentation/3.4/zh/manual/config/items/itemtypes/snmptrap).

Log in to the Zabbix CLI.

Configure the Zabbix server or proxy server and edit the **zabbix\_server.conf** file.

1. Run the following command to open the **zabbix\_server.conf** file:

**vi** *zabbix\_server.conf file path*

Example: **vi /etc/zabbix/zabbix\_server.conf**

1. Edit the **zabbix\_server.conf** file.

StartSNMPTrapper=1   
SNMPTrapperFile=[TRAP FILE]

Run the following command to restart the Zabbix service:

**systemctl restart zabbix-server**

Log in to the [official Huawei website](https://support.huawei.com/enterprise/en/intelligent-servers/e9000-chassis-pid-19961380/software?enterpriseserver=old) to obtain the MIB file and add the file to the **/usr/share/snmp/mibs** directory.

Run the **vi /etc/snmp/snmp.conf** command to create the **/etc/snmp/snmp.conf** file and add the following content to the file:

mibdirs /usr/share/snmp/mibs   
mibs +ALL   
defversion 2c

Configure the **snmptrapd.conf** file.

1. Run the following command to open the **snmptrapd.conf** file:

**vi** *snmptrapd.conf file path*

Example: **vi /etc/snmp/snmptrapd.conf**

1. Configure the **snmptrapd.conf** file.

* Configure SNMPv2c or SNMPv3.
  1. # Configure SNMPv2c as follows:

authCommunity log,execute,net [SNMP trap community name]

* 1. # Configure SNMPv3 as follows:

createUser -e [SNMPv3 engine ID] [SNMP trap V3 user name] [SHA/MD5] [Authentication password] [AES/DES] [Encryption password]   
authUser log,execute,net [SNMP trap V3 user name]

* # Add SNMPTT as the trap processing program.

traphandle default /usr/sbin/snmptthandler

Run the following command to restart snmptrapd:

**systemctl status snmptrapd**

Configure SNMPTT and edit the **snmptt.ini** file.

1. Run the following command to open the **snmptt.ini** file:

**vi** *snmptt.ini file path*

Example: **vi /etc/snmp/snmptt.ini**

1. Edit the **snmptt.ini** file.

log\_enable = 1   
log\_file = [TRAP FILE]   
date\_time\_format = %Y/%m/%d %H:%M:%S   
net\_snmp\_perl\_enable = 1   
translate\_log\_trap\_oid = 2



* **0**: displays the OID as a number.
* **1**: displays the OID name.
* **2**: displays the name of the module to which the OID belongs and the module name.

Set the SNMP trap format and edit the **snmptt.conf** file.

1. Run the following command to open the **snmptt.conf** file:

**vi** *snmptt.conf file path*

Example: **vi /etc/snmp/snmptt.conf**

1. Edit the **snmptt.conf** file.

EVENT general .\* "General Event" Normal   
FORMAT ZBXTRAP $aA $+\*

Run the following command to restart SNMPTT:

**systemctl restart snmptt**

----End



For details about SNMPTT, see the [official SNMPTT website](http://snmptt.sourceforge.net/docs/snmptt.shtml#Command-line-arguments).

## Importing a Template

### Importing a ValueMap Template



The EMM/SWI does not involve this template.

Log in to GitHub and obtain the **Huawei Server ValueMap V1.2.xml** template.

Log in to the Zabbix WebUI.

Choose **Administration > General**.

Select **Value Mapping** from the drop-down list box in the upper right corner.

Click **Import**. The **Import** page is displayed.

Click **Import file** and select the template obtained in [Step 1](#li14212161522317).

Click **Import**.

----End

### Importing an iBMC, HMM, CCU, EMM, or SWI Template



The imported template is for reference only. You can modify it as required.

Log in to GitHub and obtain the **Huawei Server iBMC Template V1.2.xml**, **Huawei Server HMM Template V1.2.xml**, **Huawei CCU Template V1.2.xml**, **Huawei Chassis EMM Template V1.2.xml**, or **Huawei Chassis SWI Template V1.2.xml** template.

Log in to the Zabbix WebUI.

Choose **Configuration > Templates**. The **Templates** page is displayed.

Click **Import**. The **Import** page is displayed.

Click **Import file** and select the template obtained in [Step 1](#li12241127163910).

Click **Import**.

----End

## Configuring a Template

### Configuring the Huawei Server HMM Template or Huawei Server iBMC Template

Log in to the Zabbix WebUI.

Choose **Configuration > Templates**. The **Templates** page is displayed.

Click the name of the iBMC or HMM template that has been imported. The template configuration page is displayed.

Click **Macros** and set **{$SNMP\_COMMUNITY}** and **{$SNMP\_PORT}**.

* The value of **{$SNMP\_COMMUNITY}** is the community name configured in 3.1.1 Configuring the iBMC or HMM.
* Retain the default value 161 for **{$SNMP\_PORT}**.

Click **Update**.

----End

### Configuring the Huawei CCU Template

Log in to the Zabbix WebUI.

Choose **Configuration > Templates**. The **Templates** page is displayed.

Click the name of the Huawei CCU Template that has been imported. The template configuration page is displayed.

Click the **Macros** tab and set **{$SNMP\_AESPASS}**, **{$SNMP\_SHAPASS}**, **{$SNMP\_USERNAME}**, and **{$SNMP\_PORT}**.

* **{$SNMP\_AESPASS}**, **{$SNMP\_SHAPASS}**, and **{$SNMP\_USERNAME}** indicate the CCU SNMPv3 encryption key, authentication key, and user name configured in 3.1.2 Configuring the CCU.
* Retain the default value 161 for **{$SNMP\_PORT}**.

Click **Update**.

----End

## Adding a Host

Log in to the Zabbix WebUI.

Choose **Configuration > Hosts**. The **Hosts** page is displayed.

Click **Create host**. The page for creating a host is displayed.

**Host** sheet:

* **Host name**: Enter the host name.
* **Groups**: Select **Huawei Server**, **Huawei Chassis** or **Huawei CCU**.



* iBMC or HMM: Select **Huawei Server**.
* CCU: Select **Huawei CCU**.
* EMM or SWI: Select **Huawei Chassis.**
* **Agent interfaces**: Click **Remove** to remove the existing IP address information.
* **SNMP interfaces**: Click , set the IP address of the iBMC, CCU, HMM, EMM, or SWI and retain the default port number **161**.



* **Enabled**: Retain the default value.

**Templates** sheet**:**

* **Link new templates**: Click **Select**. In the upper right corner of the displayed page, select the corresponding group (**Huawei Server**, **Huawei Chassis**, or **Huawei CCU**) and select the required template. After the selection is complete, click .



**Inventory** sheet:

* Select **Automatic**.



The EMM/SWI does not involve the **Inventory** tab page.

Click .



----End

# Zabbix share

* [Huawei Server iBMC Template](https://share.zabbix.com/cat-server-hardware/huawei/huawei-server-ibmc-template)
* [Huawei Server HMM Template](https://share.zabbix.com/cat-server-hardware/huawei/huawei-server-hmm-template)